NEO 8000e Site Survey Form

Email completed Survey Forms to claims@overlandstorage.com

Record of Revisions

| Description | Author | Version | Date |
| --- | --- | --- | --- |
| Original draft | Dan Davies | 1.0 | 1/4/2004 |
| Corrected Library Dimensions | Dan Davies | 1.01 | 1/5/2004 |
| Added System Configuration Section | Dan Davies | 1.02 | 1/6/2004 |
| Added Table of Contents | Dan Davies | 1.03 | 1/6/2004 |
| Added Introduction Section 1 and improved formatting | Dan Davies | 1.04 | 1/7/2004 |
| Added pallet dimensions to Section 6 and Optional Service Offerings as Section 13 | Dan Davies | 1.05 | 1/17/2004 |
| Added Customer Input to Section 17, System Environment. Optimized graphics to reduce file size. | Dan Davies | 1.06 | 6/29/2004 |
| Added metric values, branding changes, NEO 8000e | Dan Davies | 1.07 | 3/15/2011 |

Table of Contents

1.	    Introduction	3

2.	    Customer Contact Information	4

3.	    Partner Contact Information	4

4.	    Overland Contact Information	4

5.	    Overland ASP Contact Information	4

6.	    Delivery Location Information	5

7.	    Delivery Route Information	6

8.  	    Equipment Room Information	6

9.	    Library Physical Specifications	7

10.	Library Dimensional Drawings	7

11.	Library Operational Specifications	8

12.	Optional Installation Requirements:	8

13.	Optional Service Offerings:	8

14.	Configuration Information:	9

15.	Cabling Requirements:	9

16.	Library Internal Interconnect Diagram	10

17.	System Environment	11

18.	Library Backup System Interconnect Diagram	12

19.	Additional Comments:	13

20.	Additional Attachments or Diagrams:	13

# Introduction

The NEO 8000e Site Survey Form is a pre-installation survey and planning document for new installations of the NEO 8000e.

This document includes library specifications, site requirements, and guidelines to facilitate the installation of the NEO 8000e Tape Library at the customer location.

To ensure a successful installation, all sections on this form should be completed prior to deployment of the library equipment in the customer system environment.

Certain sections must be provided by the customer or authorized agent prior to equipment delivery.  Some sections may be edited or updated collaboratively during a pre-installation interview or site inspection.  Other sections will be updated by the Overland Authorized Installer during the library installation and system integration process.

The following table outlines the parties responsible for completing each section of the Site Survey Form.

| Site Survey Section | Responsible Party |
| --- | --- |
| 2 | Customer Contact Information | Overland Sales Administration |
| 3 | Partner Contact Information | Overland Sales Administration |
| 4 | Overland Contact Information | Overland Sales Administration |
| 5 | Overland ASP Contact Information | Overland Sales Administration |
| 6 | Delivery Location Information | Customer / Authorized Agent |
| 7 | Delivery Route Information | Customer / Authorized Agent |
| 8 | Equipment Room Information | Customer / Authorized Agent |
| 9 | Library Physical Specifications | Overland Storage |
| 10 | Library Dimensional Drawings | Overland Storage |
| 11 | Library Operational Specifications | Overland Storage |
| 12 | Optional installation requirements | Overland Sales Administration |
| 13 | Optional service offerings | Overland Sales Administration |
| 14 | Configuration Information | Overland Authorized Installer |
| 15 | Cabling Requirements | Overland Authorized Installer |
| 16 | Library Internal Interconnect Diagram | Overland Authorized Installer |
| 17 | System Environment | Customer / Installer |
| 18 | Library Backup System Interconnect Diagram | Overland Authorized Installer |
| 19 | Additional Comments | As Required |
| 20 | Additional Attachments or Diagrams | As Required |

# Customer Contact Information

| Contact Name |  |
| --- | --- |
| Company |  |
| Address |  |
| City |  |
| State |  |
| Country |  |
| Phone |  |
| Email |  |

# Partner Contact Information

| Contact Name |  |
| --- | --- |
| Company |  |
| Address |  |
| City |  |
| State |  |
| Country |  |
| Phone |  |
| Email |  |

# Overland Contact Information

| Sales Contact |  |
| --- | --- |
| Sales Phone # |  |
| Sales Email |  |
| Technical Contact |  |
| Technical Phone # |  |
| Technical Email |  |

# Authorized Service Provider Contact Information

| ASP Contact |  |
| --- | --- |
| ASP Phone # |  |
| ASP Email |  |

# Delivery Location Information

| Planned Delivery Date and Time |  |
| --- | --- |
| Planned Installation Date and Time |  |
| Planned Operational Date and Time |  |
| Loading Dock contact |  |
| Access requirements for unpacking team (badges, passes, clearances) |  |
| Scheduling requirements for Delivery Location? |  |
| Semi-trailer accessibility? |  |
| Loading Dock Specifications (loading dock, type of ramps, weather protection) |  |
| Location for unpacking |  |
| Special tools required for uncrating | 9/16” Box Wrench, Strap Cutter |

NEO8000e Unpacking Dimensions & Required Clearances

# Delivery Route Information

| Method of transport to Equipment Room (forklift, pallet jack, casters) |  |
| --- | --- |
| Access to Equipment Room (smallest door dimensions, elevator dimensions, stairs, ramp locations, incline dimensions, carpeting, floor type(s) transited) |  |
| Aisle and Door Clearances |  |
| Shipping Container and Pallet Dimension Specifications (Height, Width, Depth, Front/Rear clearances for unpacking) | See Drawings Previous Page |

# Equipment Room Information

| Equipment Room Contact? |  |
| --- | --- |
| Access requirements for installation team (badges, passes, security clearances) |  |
| Scheduling requirements for Equipment Room Location? |  |
| Room Dimension |  |
| Ceiling Dimension |  |
| Aisle and Door Clearances |  |
| Floor Type (raised/non-raised floor) |  |
| Floor Load Capacity (recommended floor load rating? – lb/ft2) |  |
| Library Location in Equipment Room |  |
| Power Connection Locations (wall, floor, , sub-floor, overhead, ceiling, etc.) |  |
| Interface Cabling Locations (wall, floor, , sub-floor, overhead, ceiling, etc.) |  |
| Fire Protection Considerations? |  |
| UPS Considerations? |  |

# Library Physical Specifications

| Library Height | 76 inches (193cm) |
| --- | --- |
| Library Width | 24 inches (61cm) |
| Library Depth (without rear door) | 41.5 inches (106cm) |
| Library Depth (with rear door) | 43 inches (109cm) |
| Library Front clearance required | 24 inches (61cm) |
| Library Rear clearance required | 24 inches (61cm) |
| Library Weight (min-max) | 655-995 lb. (297-451kg) |
| Leveling required? |  |

# Library Dimensional Drawings

#### Top View		  Front View	         Side View

C1 (Caster)	18.0” (46 cm)		C2 (Caster)    33.75”  (86 cm)

L1 (Leveler)	22.375” (57 cm)	L2 (Leveler)  38.375”(97 cm)

Front View			     Side View

Caster and Leveler Locations

# Library Operational Specifications

| Operational temperature | 10o C - 40o C (dry bulb) |
| --- | --- |
| Operational humidity | 15% - 85% (non-condensing) |
| Thermal Rating (maximum configuration): | 2180 BTU - 640 Watts |
| Voltage | 100-120, 200-240 VAC auto-ranging |
| Amperage (maximum configuration) | 9 a (100-120 VAC) 4.5 a (200-240 VAC) |
| Power connector types (100-120 VAC) | Power connection - NEMA 5-15P Library connection - IEC 60320 C19 |
| Power connector types (200-240 VAC) | Power connection - Not Supplied (Country specific) Library connection - IEC 60320 C19 |
| Power cable lengths (100-120 VAC) | 9 feet (2.7m) |
| Acoustic Specification – Idling | 6.4 bels maximum |
| Acoustic Specification - Operational | 7.0 bels maximum |

# Optional Installation Requirements:

| Additional Tape Drives |  |
| --- | --- |
| Interface Options |  |
| Capacity Option |  |

# Optional Service Offerings:

| P/N NEO 8000e | P/N Add-on Drive | Description | Y/N |
| --- | --- | --- | --- |

# Configuration Information:

| User 1 Password |  |
| --- | --- |
| User 2 Password |  |
| Service Password |  |
| WebTLC Level 1 Password |  |
| WebTLC Level 2 Password |  |
| WebTLC IP Address |  |
| WebTLC Subnet Mask |  |
| WebTLC Gateway Address |  |
| WebTLC Email Configuration |  |
| WebTLC SNMP Configuration |  |
| FCO Link Speed |  |
| FCO Topology |  |
| FCO Address Mapping |  |
| Partitioning Configuration |  |

# Cabling Requirements:

| LVD SCSI Connector Type(s) | VHDCI-68 |
| --- | --- |
| LVD SCSI Cabling Required |  |
| Fibre Channel Interface Connector Type(s) | LC |
| Fibre Channel Cabling Required |  |
| SAS Interface Option Connector Type(s) | Mini-SAS (SFF-8088) |
| SAS Interface Cabling Required |  |

# Library Internal Interconnect Diagram

# System Environment

Library System Attachment Summary (Backup Network):

#### Backup Server #1 Information

| Operating System |  |
| --- | --- |
| Host Bus Adapter |  |
| HBA Interface Type |  |
| HBA Firmware Revision |  |
| HBA Driver Revision |  |
| Backup Software |  |
| Backup Software Version |  |
| Backup Software Options |  |

#### Additional Backup/Media Server Information

| Operating System |  |
| --- | --- |
| Host Bus Adapter |  |
| HBA Interface Type |  |
| HBA Firmware Revision |  |
| HBA Driver Revision |  |
| Backup Software |  |
| Backup Software Vendor |  |
| Backup Software Version |  |
| Backup Software Options |  |

#### Fibre Channel Switch Information (for Fibre-attached libraries

| Model |  |
| --- | --- |
| Firmware Revision |  |

Disk Subsystem Information (SAN-attached storage)

| Fibre Disk Model |  |
| --- | --- |
| Fibre Disk Revision |  |

SAN Host System Information (For Non-Backup/Media Servers on SAN)

| Fibre HBA Model |  |
| --- | --- |
| Host Operating System |  |
| Host Bus Adapter |  |
| HBA Firmware Revision |  |
| HBA Driver Revision |  |

# Library Backup System Interconnect Diagram

Attach a diagram of the final library/system configuration here.  Following is an example of some of the information to be included in this system interconnect diagram.

# Additional Comments:

# Additional Attachments or Diagrams:

# Text boxes

## CONFIGURATION INFORMATION

| Library |  |
| --- | --- |
| Library IP Address |  |

| Drive 1 |  |
| --- | --- |
| Drive 2 |  |
| Drive 3 |  |
| Drive 4 |  |
| Drive 5 |  |
| Drive 6 |  |
| Drive 7 |  |
| Drive 8 |  |
| Drive 9 |  |
| Drive 10 |  |
| Drive 11 |  |
| Drive 12 |  |

| Server Configuration Info |
| --- |
| Server A Information | O/S, WWN, etc. |
| Server B Information | O/S, WWN, etc. |
| Server C Information | O/S, WWN, etc. |
| Switch Configuration Info |
| Switch | Name Server |
| FCO Configuration Info |
| FCO #1 Config | WWN, Mapping, etc. |
| FCO #2 Config | WWN, Mapping, etc. |
| FCO #3 Config | WWN, Mapping, etc. |